## Runtime
Runtimes in minutes
| 9E1000I |  | 9E2000I | [5 empty] | 9E3000I | [5 empty] | 9E3000IXL
| Watts | UPS | Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM | Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM | Watts | 1 EBM | 2 EBM | 3 EBM | 4 EBM
| 40 | 117.5 | 80 | 228 | 833.4 | 1800 | 2400 | 2400 | 120 | 180 | 699.9 | 1320 | 2143.2 | 2400 | 120 | 399.9667 | 900 | 1800 | 2400
| 80 | 56 | 150 | 110 | 386.6333 | 759.9 | 1114.2 | 1732.8 | 240 | 85.2667 | 270 | 528 | 814.2 | 1100.1 | 240 | 180 | 399.9667 | 699.9 | 900
| 120 | 40 | 200 | 84.3667 | 285 | 552 | 828.6 | 1133.4 | 360 | 54 | 185.7 | 330 | 480 | 722.1 | 360 | 115 | 235.7333 | 413.2833 | 624.9
| 160 | 30 | 250 | 65.6333 | 227.3333 | 423.9667 | 685.8 | 866.7 | 480 | 41 | 137.7667 | 229.7333 | 360 | 475.5667 | 480 | 89.2167 | 190.7333 | 295.0167 | 425.0333
| 200 | 24.5333 | 300 | 54.7 | 198.9667 | 354 | 548.5167 | 766.8 | 600 | 30.4833 | 107.5 | 190.2667 | 261.4167 | 373.3167 | 600 | 71.0333 | 150 | 222.8333 | 322.5
| 240 | 21.7333 | 350 | 46.7667 | 173.5833 | 300 | 451.4333 | 666.6 | 720 | 26.3 | 88.4167 | 156 | 216.7167 | 289.9833 | 720 | 55 | 116.2333 | 188.5833 | 237.8333
| 280 | 17.6333 | 400 | 41 | 152.1667 | 250.0167 | 394.3167 | 546.7167 | 840 | 21.5167 | 76.8333 | 126.6667 | 189.7833 | 233.3333 | 840 | 44.6667 | 102.5 | 162.2333 | 214.2667
| 320 | 14.3667 | 450 | 35.2833 | 130.7333 | 225.4833 | 342.8333 | 457.8 | 960 | 18.1333 | 65.25 | 111.5 | 166.6833 | 212.4 | 960 | 41 | 89.2167 | 137.7667 | 190.7333
| 360 | 12.8167 | 500 | 30.5667 | 116.3667 | 209.1 | 304.2667 | 417.7167 | 1080 | 15.3667 | 56 | 100.5 | 145.7333 | 191.4 | 1080 | 36.1833 | 80.5167 | 117.5 | 169.9833
| 400 | 11.6 | 550 | 25.5 | 107.2833 | 190.9167 | 266.2833 | 373.3167 | 1200 | 13.3667 | 49 | 90 | 125.7 | 173.3333 | 1200 | 31.1833 | 72.2333 | 108.7667 | 152.5167
| 440 | 10 | 600 | 23.8833 | 102.7167 | 181.8 | 247.5 | 353.3333 | 1320 | 11.5333 | 43.8833 | 83.0333 | 114.2833 | 157.0167 | 1320 | 27.9667 | 63.5333 | 99.5833 | 134.1667
| 480 | 8.7333 | 650 | 21.6667 | 95.8333 | 170.8833 | 232.3167 | 326.6333 | 1440 | 10.0667 | 41.45 | 76.1167 | 106.4167 | 140.7667 | 1440 | 25.35 | 56.75 | 90.4167 | 118.4333
| 520 | 7.35 | 700 | 19.4667 | 88.8833 | 159.1167 | 220.8667 | 297 | 1560 | 8.95 | 38.7333 | 69.4833 | 98.9333 | 125.1667 | 1560 | 22.85 | 51.5 | 84.75 | 111.8833
| 560 | 6.9 | 750 | 17.85 | 83.8833 | 147.4167 | 209.3333 | 270 | 1680 | 8 | 35.2333 | 62.5167 | 91.0667 | 115.8333 | 1680 | 20.2333 | 46 | 78.9667 | 105
| 600 | 6.4667 | 800 | 16.25 | 78.9 | 135.6667 | 197.8833 | 243 | 1800 | 7.2167 | 31.75 | 57.2 | 85.7167 | 109.7167 | 1800 | 18.6167 | 43.5 | 73.1667 | 98.1167
| 640 | 6.05 | 850 | 14.8833 | 74.4333 | 125.2167 | 187.6833 | 233.1 | 1920 | 6.55 | 29.1333 | 52.8 | 80.7667 | 103.6167 | 1920 | 17.0833 | 41.6667 | 67.3833 | 91.25
| 680 | 5.6333 | 900 | 13.8 | 69.45 | 117.3667 | 177.1833 | 224.2833 | 2040 | 5.95 | 27.3833 | 48.4 | 75.7833 | 97.5 | 2040 | 15.55 | 39.7667 | 61.5833 | 86.4667
| 720 | 5.2333 | 1000 | 11.6667 | 59.35 | 107.3667 | 159.3667 | 205.5667 | 2160 | 5.4833 | 25.6333 | 44.6667 | 70.8333 | 91.3833 | 2160 | 14.3 | 37.1333 | 57.3333 | 82.1167
| 760 | 4.8333 | 1100 | 10.25 | 53.9333 | 98.5 | 143.4667 | 188.8833 | 2280 | 5 | 23.8167 | 43.1333 | 65.6333 | 86.85 | 2280 | 13.15 | 34.4 | 53.5 | 77.5833
| 800 | 4.5 | 1200 | 9.8833 | 48.2 | 89.6667 | 126.5333 | 173.4 | 2400 | 4.6667 | 22.0667 | 41.6667 | 60.6833 | 82.9833 | 2400 | 12.05 | 31.7833 | 49.8333 | 73.2333
|  |  | 1300 | 8.8 | 44 | 83.7833 | 115.9167 | 160.2667
|  |  | 1400 | 7.7 | 41.6333 | 77.6167 | 108.8833 | 146.3333
|  |  | 1500 | 6.9667 | 39.15 | 71.7333 | 102.2167 | 133.2
|  |  | 1600 | 6.3667 | 35.9333 | 65.55 | 95.3667 | 119.7167

## Source
for VA=W loads (unit=minutes)
9E (% of rated load) | 5 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
1000 | 117.5 | 56 | 30 | 21.7333 | 14.3667 | 11.6 | 8.7333 | 6.9 | 6.05 | 5.2333 | 4.5
2000 | 228 | 103.3333 | 52.0667 | 32.7833 | 22.2167 | 16.25 | 12.4833 | 10.8833 | 9 | 7.4167 | 6.4
3000 | 180 | 85.2667 | 41 | 26.3 | 18.1333 | 13.3667 | 10.0667 | 8 | 6.55 | 5.4833 | 4.6667
2000 + 1 EBM | 833.4 | 360 | 189.4833 | 120 | 97.5 | 78.9 | 63.3333 | 52.6667 | 44.3667 | 40.75 | 36.1
2000 + 2 EBM | 1800 | 720 | 336 | 216.3667 | 173.4667 | 135.6667 | 111.5833 | 96.5 | 84.7833 | 75.3333 | 65.8833
2000 + 3 EBM | 2400 | 1028.7 | 497.1667 | 321.4167 | 234.9 | 197.8833 | 166.8667 | 139.6833 | 117.0333 | 106.3 | 95.3667
2000 + 4 EBM | 2400 | 1599.6 | 733.2 | 435.6 | 333.3667 | 243 | 213.4167 | 184.9167 | 162.4167 | 141.2333 | 120
3000 + 1 EBM | 699.9 | 270 | 137.7667 | 88.4167 | 65.25 | 49 | 41.45 | 35.2333 | 29.1333 | 25.6333 | 22.0667
3000 + 2 EBM | 1320 | 528 | 229.7333 | 156 | 111.5 | 90 | 76.1167 | 62.5167 | 52.8 | 44.6667 | 41.6667
3000 + 3 EBM | 2143.2 | 814.2 | 360 | 216.7167 | 166.6833 | 125.7 | 106.4167 | 91.0667 | 80.7667 | 70.8333 | 60.6833
3000 + 4 EBM | 2400 | 1100.1 | 475.5667 | 289.9833 | 212.4 | 173.3333 | 140.7667 | 115.8333 | 103.6167 | 91.3833 | 82.9833
3000XL + 1 EBM | 399.9667 | 180 | 89.2167 | 55 | 41 | 31.1833 | 25.35 | 20.2333 | 17.0833 | 14.3 | 12.05
3000XL + 2 EBM | 900 | 399.9667 | 190.7333 | 116.2333 | 89.2167 | 72.2333 | 56.75 | 46 | 41.6667 | 37.1333 | 31.7833
3000XL + 3 EBM | 1800 | 699.9 | 295.0167 | 188.5833 | 137.7667 | 108.7667 | 90.4167 | 78.9667 | 67.3833 | 57.3333 | 49.8333
3000XL + 4 EBM | 2400 | 900 | 425.0333 | 237.8333 | 190.7333 | 152.5167 | 118.4333 | 105 | 91.25 | 82.1167 | 73.2333
actual runtime may vary from 0-30% around these typical values

## 1000
actual runtime may vary from 0-30% around these typical values

## 2000
actual runtime may vary from 0-30% around these typical values

## 2000+EBM
actual runtime may vary from 0-30% around these typical values

## 3000
actual runtime may vary from 0-30% around these typical values

## 3000+EBM
actual runtime may vary from 0-30% around these typical values

## 3000XL+EBM
actual runtime may vary from 0-30% around these typical values