## Runtime
Runtimes in minutes
| 9PX1000 | [5 empty] | 9PX1500 | [5 empty] | 9PX2200 | [5 empty] | 9PX3000
| Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM | Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM | Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM | Watts | UPS | 1 EBM | 2 EBM | 3 EBM | 4 EBM
| 50 | 162.68 | 751.9 | 1431.3 | 2167 | 2947 | 75 | 145.53 | 542.3 | 997 | 1492.7 | 2016.9 | 110 | 120.492 | 562.195 | 1072.031 | 1624.79 | 2209.625 | 150 | 115.056 | 428.409 | 789.339 | 1180.507 | 1594.67
| 75 | 109.291 | 509.3783 | 971.9873 | 1472.6785 | 2004.1324 | 100 | 110.7108 | 410.7963 | 755.3526 | 1130.9703 | 1528.1116 | 150 | 88.2933 | 414.2381 | 791.0471 | 1199.6837 | 1632.0462 | 200 | 88.0792 | 327.4763 | 603.2562 | 902.2154 | 1218.7668
| 100 | 81.5645 | 384.5832 | 735.1835 | 1114.5454 | 1517.4762 | 125 | 88.5255 | 328.8046 | 604.6286 | 905.3351 | 1223.2272 | 200 | 65.0834 | 308.9387 | 590.8689 | 896.6779 | 1220.2586 | 300 | 59.4516 | 221.4706 | 408.0242 | 610.229 | 824.3251
| 125 | 65.3047 | 311.073 | 595.4379 | 903.1 | 1229.9801 | 150 | 73.704 | 274.6543 | 505.0461 | 756.2495 | 1021.7851 | 250 | 51.422 | 246.9241 | 472.822 | 717.8851 | 977.2041 | 400 | 45.1252 | 168.2047 | 309.9683 | 463.5747 | 626.2085
| 150 | 54.6733 | 262.2806 | 502.5467 | 762.4926 | 1038.72 | 175 | 63.315 | 236.7211 | 435.2621 | 651.7686 | 880.6174 | 300 | 42.5977 | 206.2754 | 395.3484 | 600.4814 | 817.5593 | 500 | 36.3831 | 135.3439 | 249.436 | 373.0434 | 503.9197
| 175 | 47.1133 | 226.9393 | 435.1932 | 660.5089 | 899.9611 | 200 | 55.6906 | 208.6541 | 383.6145 | 574.4365 | 776.1355 | 350 | 36.4196 | 177.2223 | 339.9172 | 516.4453 | 703.2626 | 600 | 30.2911 | 112.4728 | 207.2661 | 309.977 | 418.7366
| 200 | 41.4078 | 199.8373 | 383.5027 | 582.221 | 793.4251 | 225 | 49.8561 | 186.8968 | 343.5707 | 514.4754 | 695.126 | 400 | 31.8093 | 155.1415 | 297.7542 | 452.5041 | 616.2824 | 700 | 25.7028 | 95.544 | 176.0312 | 263.2658 | 355.645
| 225 | 36.9197 | 178.2844 | 342.3696 | 519.9082 | 708.6175 | 250 | 45.2245 | 169.3927 | 311.3523 | 466.2297 | 629.946 | 450 | 28.2002 | 137.6611 | 264.3546 | 401.8404 | 547.3551 | 800 | 22.0884 | 82.583 | 152.1104 | 227.4933 | 307.3259
| 250 | 33.2822 | 160.7223 | 308.833 | 469.0921 | 639.4487 | 275 | 41.4315 | 154.905 | 284.6858 | 426.2964 | 575.9969 | 500 | 25.2729 | 123.4437 | 237.1757 | 360.6045 | 491.2481 | 900 | 19.1621 | 72.4298 | 133.3732 | 199.4729 | 269.4749
| 275 | 30.2664 | 146.1546 | 280.9984 | 426.9063 | 582.0199 | 300 | 38.2434 | 142.6553 | 262.1402 | 392.5332 | 530.3836 | 550 | 22.8355 | 111.6607 | 214.6408 | 326.4081 | 444.7149 | 1000 | 16.7505 | 64.3236 | 118.4201 | 177.1115 | 239.2652
| 300 | 27.7198 | 133.8963 | 257.5624 | 391.3789 | 533.6489 | 325 | 35.5058 | 132.1299 | 242.7699 | 363.5248 | 491.1937 | 600 | 20.7654 | 101.7563 | 195.691 | 297.6469 | 405.5741 | 1100 | 14.7385 | 57.7382 | 106.2805 | 158.9571 | 214.737
| 325 | 25.5367 | 123.4529 | 237.5843 | 361.0866 | 492.3997 | 350 | 33.1135 | 122.9729 | 225.9205 | 338.2912 | 457.1029 | 650 | 18.9803 | 93.3345 | 179.5717 | 273.1774 | 372.2707 | 1200 | 13.0451 | 52.2992 | 96.2632 | 143.9764 | 194.4952
| 350 | 23.6407 | 114.4564 | 220.364 | 334.9702 | 456.8316 | 375 | 30.9932 | 114.9273 | 211.1185 | 316.1237 | 427.1539 | 700 | 17.4229 | 86.1015 | 165.7228 | 252.1506 | 343.6503 | 1300 | 11.6104 | 47.7371 | 87.8692 | 131.4231 | 177.5325
| 375 | 21.9754 | 106.6276 | 205.3702 | 312.2253 | 425.8507 | 400 | 29.0923 | 107.8006 | 198.0091 | 296.491 | 400.6288 | 750 | 16.0513 | 79.8334 | 153.7169 | 233.9191 | 318.8323 | 1400 | 10.3884 | 43.8552 | 80.7348 | 120.7533 | 163.1146
| 400 | 20.4986 | 99.7513 | 192.1933 | 292.2326 | 398.6149 | 425 | 27.3725 | 101.4439 | 186.3183 | 278.9829 | 376.9734 | 800 | 14.8344 | 74.3562 | 143.2223 | 217.9798 | 297.1326 | 1500 | 9.3432 | 40.5093 | 74.5924 | 111.5667 | 150.701
| 425 | 19.1778 | 93.6602 | 180.515 | 274.5101 | 374.4685 | 450 | 25.8048 | 95.7396 | 175.8294 | 263.2747 | 355.7492 | 850 | 13.7483 | 69.5332 | 133.9779 | 203.937 | 278.0129 | 1600 | 8.4459 | 37.5922 | 69.2433 | 103.5665 | 139.891
| 450 | 17.9879 | 88.2228 | 170.0851 | 258.6794 | 352.8968 | 475 | 24.3675 | 90.5932 | 166.3679 | 249.1053 | 336.6035 | 900 | 12.7741 | 65.2557 | 125.7761 | 191.4761 | 261.0455 | 1700 | 7.6732 | 35.0238 | 64.5388 | 96.5301 | 130.3839
| 475 | 16.909 | 83.3352 | 160.7057 | 244.4408 | 333.4925 | 500 | 23.0433 | 85.9272 | 157.7915 | 236.2614 | 319.2482 | 1000 | 11.1037 | 58.006 | 111.8685 | 170.3418 | 232.2641 | 1800 | 7.0058 | 32.7434 | 60.3663 | 90.2892 | 121.9522
| 500 | 15.9256 | 78.9145 | 152.2189 | 231.5555 | 315.9306 | 525 | 21.8189 | 81.678 | 149.9825 | 224.5668 | 303.4455 | 1100 | 9.7317 | 52.0926 | 100.517 | 153.0874 | 208.7626 | 1900 | 6.4278 | 30.7045 | 56.6393 | 84.7145 | 114.4214
| 525 | 15.0248 | 74.8941 | 144.4981 | 219.8315 | 299.95 | 550 | 20.6831 | 77.7923 | 142.843 | 213.875 | 288.9971 | 1200 | 8.5937 | 47.1734 | 91.0687 | 138.7227 | 189.194 | 2000 | 5.926 | 28.8711 | 53.2909 | 79.706 | 107.656
| 550 | 14.1966 | 71.2202 | 137.4404 | 209.1134 | 285.3393 | 575 | 19.627 | 74.2256 | 136.2907 | 204.0625 | 275.7367 | 1300 | 7.6422 | 43.0158 | 83.0788 | 126.5732 | 172.641 | 2100 | 5.4894 | 27.2146 | 50.2681 | 75.1846 | 101.5492
| 575 | 13.4324 | 67.8488 | 130.9622 | 199.2743 | 271.9258 | 600 | 18.643 | 70.9402 | 130.2562 | 195.0255 | 263.5239 | 1400 | 6.8415 | 39.4573 | 76.2372 | 116.1683 | 158.4631 | 2200 | 5.1086 | 25.7123 | 47.5289 | 71.087 | 96.0155
| 600 | 12.7253 | 64.7439 | 124.9945 | 190.2098 | 259.5677 | 625 | 17.7247 | 67.904 | 124.6803 | 186.6755 | 252.2391 | 1500 | 6.1641 | 36.3816 | 70.3215 | 107.1706 | 146.2016 | 2300 | 4.7758 | 24.3457 | 45.0388 | 67.3622 | 90.9856
| 625 | 12.0693 | 61.8754 | 119.4802 | 181.8333 | 248.147 | 650 | 16.8666 | 65.0896 | 119.5128 | 178.9369 | 241.7803 | 1600 | 5.588 | 33.7033 | 65.1682 | 99.3319 | 135.5185 | 2400 | 4.4843 | 23.0996 | 42.7696 | 63.9677 | 86.4023
| 650 | 11.4596 | 59.2183 | 114.3714 | 174.0724 | 237.565 | 675 | 16.0636 | 62.4737 | 114.7102 | 171.7449 | 232.0601 | 1700 | 5.096 | 31.3577 | 60.6536 | 92.4643 | 126.1582 | 2500 | 4.2284 | 21.961 | 40.6975 | 60.868 | 82.2176
| 675 | 10.8918 | 56.7515 | 109.6278 | 166.8657 | 227.7384 | 700 | 15.3116 | 60.0359 | 110.2353 | 165.0437 | 223.003 | 1800 | 4.6741 | 29.2946 | 56.6818 | 86.4219 | 117.9222 | 2600 | 4.0034 | 20.9193 | 38.8026 | 58.0333 | 78.3908
| 700 | 10.3624 | 54.4568 | 105.2147 | 160.1611 | 218.596 | 725 | 14.6067 | 57.7587 | 106.0558 | 158.7849 | 214.5436 | 1900 | 4.3112 | 27.474 | 53.1761 | 81.0887 | 110.6524 | 2700 | 3.805 | 19.9649 | 37.0674 | 55.4376 | 74.887
| 725 | 9.868 | 52.319 | 101.1027 | 153.9135 | 210.0767 | 750 | 13.9455 | 55.6269 | 102.1437 | 152.9265 | 206.6252 | 2000 | 3.9979 | 25.8636 | 50.0746 | 76.37 | 104.22 | 2800 | 3.63 | 19.0898 | 35.477 | 53.0584 | 71.6758
| 750 | 9.406 | 50.3244 | 97.2661 | 148.0842 | 202.1274 | 775 | 13.3248 | 53.6272 | 98.4744 | 147.4318 | 199.1983 | 2100 | 3.7267 | 24.4365 | 47.3254 | 72.1874 | 98.5182 | 2900 | 3.4751 | 18.2868 | 34.0182 | 50.8759 | 68.7303
| 775 | 8.9739 | 48.4615 | 93.6823 | 142.6388 | 194.7017 | 800 | 12.7417 | 51.748 | 95.0265 | 142.2686 | 192.2194 | 2200 | 3.4912 | 23.17 | 44.8854 | 68.475 | 93.4571 | 3000 | 3.3378 | 17.5495 | 32.6792 | 48.8728 | 66.0271
| 800 | 8.5693 | 46.7198 | 90.3315 | 137.5474 | 187.7585 | 825 | 12.1938 | 49.9789 | 91.7812 | 137.4087 | 185.6504
| 850 | 7.8353 | 43.5642 | 84.2604 | 128.3222 | 175.1778 | 850 | 11.6785 | 48.311 | 88.7217 | 132.8272 | 179.4575
| 900 | 7.1902 | 40.795 | 78.932 | 120.2256 | 164.1359 | 900 | 10.7373 | 45.2476 | 83.103 | 124.4133 | 168.0843
| 950 | 6.6225 | 38.3605 | 74.2476 | 113.1073 | 154.4281 | 950 | 9.9025 | 42.5035 | 78.0708 | 116.8775 | 157.898
| 1000 | 6.1225 | 36.2178 | 70.1245 | 106.8418 | 145.8833 | 1000 | 9.1608 | 40.0352 | 73.5449 | 110.1002 | 148.7367
[7 empty] | 1100 | 7.9119 | 35.7909 | 65.7639 | 98.4481 | 132.986
[7 empty] | 1200 | 6.9159 | 32.2983 | 59.3619 | 88.8611 | 120.0268
[7 empty] | 1300 | 6.1166 | 29.4031 | 54.0558 | 80.9153 | 109.286
[7 empty] | 1400 | 5.4713 | 26.9911 | 49.6356 | 74.296 | 100.3384
[7 empty] | 1500 | 4.9476 | 24.9744 | 45.94 | 68.7618 | 92.8577

## Source
for VA=W loads (unit=minutes)
9PX (% of rated load) | 5 | 10 | 20 | 30 | 40 | 50 | 60 | 70 | 80 | 90 | 100
1000 | 163 | 81 | 41 | 27 | 20 | 16.5 | 13 | 10.5 | 8.5 | 7 | 6
1500 | 145 | 74 | 38 | 25 | 19 | 14 | 10.5 | 8.5 | 7 | 6 | 5
2200 | 120 | 59 | 29 | 19 | 13.5 | 10 | 7.5 | 6 | 5 | 4 | 3.5
3000 | 115 | 60 | 30 | 20 | 13 | 9.5 | 7 | 5.5 | 4.5 | 3.5 | 3
1000 + 1 EBM | 752 | 385 | 200 | 134 | 100 | 79 | 65 | 55 | 47 | 41 | 36
1000 + 2 EBM | 1431 | 735 | 384 | 258 | 192 | 152 | 125 | 106 | 90 | 78 | 70
1000 + 3 EBM | 2167 | 1115 | 586 | 392 | 292 | 231 | 191 | 161 | 138 | 120 | 107
1000 + 4 EBM | 2945 | 1517 | 793 | 533 | 398 | 316 | 260 | 220 | 188 | 163 | 146
1500 + 1 EBM | 542 | 274 | 142 | 96 | 71 | 55 | 45 | 38 | 32 | 28 | 25
1500 + 2 EBM | 998 | 506 | 262 | 176 | 130 | 102 | 83 | 70 | 59 | 52 | 46
1500 + 3 EBM | 1493 | 756 | 392 | 263 | 195 | 153 | 124 | 104 | 89 | 77 | 69
1500 + 4 EBM | 2016 | 1021 | 530 | 356 | 263 | 206 | 168 | 141 | 120 | 105 | 93
2200 + 1 EBM | 562 | 281 | 141 | 92 | 67 | 52 | 42 | 35 | 30 | 26 | 23
2200 + 2 EBM | 1072 | 537 | 270 | 177 | 129 | 100 | 82 | 68 | 58 | 50 | 45
2200 + 3 EBM | 1625 | 815 | 411 | 269 | 196 | 153 | 124 | 104 | 89 | 77 | 69
2200 + 4 EBM | 2210 | 1109 | 560 | 366 | 267 | 208 | 170 | 142 | 121 | 105 | 94
3000 + 1 EBM | 428 | 221 | 112 | 73 | 52 | 40 | 33 | 27 | 23 | 20 | 17
3000 + 2 EBM | 789 | 408 | 207 | 134 | 96 | 74 | 60 | 51 | 43 | 37 | 33
3000 + 3 EBM | 1181 | 610 | 310 | 200 | 144 | 111 | 90 | 76 | 64 | 55 | 49
3000 + 4 EBM | 1595 | 824 | 419 | 270 | 194 | 150 | 122 | 102 | 86 | 74 | 66
actual runtime may vary from +/- 15% around these typical values

## 1000
actual runtime may vary from +/- 15% around these typical values

## 1000+EBM
actual runtime may vary from +/- 15% around these typical values

## 1500
actual runtime may vary from +/- 15% around these typical values

## 1500+EBM
actual runtime may vary from +/- 15% around these typical values

## 2200
actual runtime may vary from +/- 15% around these typical values

## 2200+EBM
actual runtime may vary from +/- 15% around these typical values

## 3000
actual runtime may vary from +/- 15% around these typical values

## 3000+EBM
actual runtime may vary from +/- 15% around these typical values